Section 083323
upward coiling Doors
model 900

NOTE: Enable Microsoft Word option to display hidden text to view notes to specifier.

PART 1 GENERAL

Section Includes

Upward coiling service doors.

Related Requirements

Section << 079200 - Joint Sealants>>:  Sealing joints between frames and adjacent construction.

Section << 083313 - Coiling Counter Doors>>:  Additional types of overhead coiling doors.

Section << 087100 - Door Hardware>>:  Cylinder cores and keys.

Section << 260583 - Wiring Connections>>:  Power to disconnect.

Reference Standards

ASHRAE Std 90.1 I-P - Energy Standard for Buildings Except Low-Rise Residential Buildings; Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.

ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process; 2023.

ASTM E90 - Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements; 2023.

ASTM E330/E330M - Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference; 2014 (Reapproved 2021).

FBC TAS 201 - Impact Test Procedures; Testing Application Standard; 1994.

FBC TAS 202 - Criteria for Testing Impact and Non-Impact Resistant Building Envelope Components Using Uniform Static Air Pressure; Testing Application Standard; 1994.

ICC (IECC)-2018 - International Energy Conservation Code; 2018.

UL (DIR) - Online Certifications Directory; Current Edition.

~~~~~ MASTER NOTE ~~~~~~
Do not request submittals if drawings sufficiently describe the products of this section or if proprietary specifying techniques are used. The review of submittals increases the possibility of unintended variations from contract documents, thereby increasing the design professional's liability.

- ~~~ END OF MASTER NOTE ~~~~

Submittals

Product Data:  Submit manufacturer's standard literature showing materials and details of construction and finish.<<  Include data on electrical operation.; or  None - N/A>>

Shop Drawings:  Indicate rough and actual opening dimensions, anchorage methods, hardware locations, and installation details.

Manufacturer's Instructions:  Indicate installation sequence and installation, adjustment, and alignment procedures.

Manufacturer's qualification statement.

Installer's qualification statement.

Operation and Maintenance Data:  Indicate modes of operation, lubrication requirements and frequency, and periodic adjustments required.

Specimen warranty.

Quality Assurance

Manufacturer Qualifications:  Company specializing in performing work of this section with minimum of << 5 years; or  _____ years>> of<<  documented;    _____; or  None - N/A>> experience in fabrication and installation of security closures.

Installer Qualifications:  Company specializing in performing work of this section with minimum of << 3 years; or  _____ years>> of<<  documented;    _____; or  None - N/A>> experience and approved by manufacturer.

Products Requiring Electrical Connection:  Listed and classified by << UL (DIR);  TUV;  testing firm acceptable to authorities having jurisdiction; or  _____>> as suitable for purpose specified.

Delivery, Storage, and Handling

Store products in manufacturer's unopened packaging until ready for installation.

Protect materials from exposure to moisture.

Store materials in dry, warm, ventilated, weathertight location.

Warranty

Manufacturer Door-Only Warranty:  Provide manufacturer warranty for door assembly for duration indicated under individual doors. Complete forms in <<Owner>>'s name and register with manufacturer.

Manufacturer Door and Operator Warranty:  Provide manufacturer's limited warranty for door and operator system free from material and workmanship defects for duration and cycles indicated under individual doors; counterbalance spring and finish not covered by warranty.

PART 2 PRODUCTS

Manufacturer

- ~~~~~ MASTER NOTE ~~~~~~
Founded in 1954, Wayne Dalton was built on a dedication to ingenuity and customer service. As our business grew, so did our commitment to expanding our product lines, leading the company to become one of the largest door manufacturers in the United States. Since the beginning, we have remained committed to being the garage door partner whose innovation drives dealer productivity and provides industry-leading garage door solutions. In continuing this innovation, Wayne Dalton offers products, not only through our dealer connections, but also through our retail partner, Lowe's. Wayne Dalton offers a broad selection of residential garage doors, as well as a complete line of doors for commercial and industrial applications. Our Commercial Sectional Doors are ideal for jobs that call for excellent thermal efficiency, have stringent wind load requirements, or simply need a high performing door designed for long life and superior strength. Our Commercial Rolling Doors include service doors, counter doors, fire doors, security grilles, security shutters and roll up sheet doors. In 2016, we expanded our commercial door category to include High Speed Doors. Wayne Dalton designed and built a new series of High-Speed Doors from the ground up. These doors feature patent-pending, high-cycle designs, and industry-leading safety features for both interior and exterior applications. With everything from residential garage doors to rolling doors to commercial sectional to high performance doors, Wayne Dalton’s breadth of product can provide a garage door solution for any application.   Contact Information: Wayne Dalton 2501 S State Hwy 121 Bus, Suite 200 Lewisville, Texas 75067 United States   Phone: (800) 827-3667 Email: info@wayne-dalton.com   Contact for Design Professional: Customer Service Phone: (800) 827-3667 Email: info@wayne-dalton.com   Online CEU Courses   Request Lunch & Learn   https://www.wayne-dalton.com/   Plant Location: Dalton, Ohio; Mt. Hope, Ohio, Pensacola, Florida; Centralia, Washington.    
~~~ END OF MASTER NOTE ~~~~

Wayne Dalton; www.wayne-dalton.com; 1 (800) 827-3667.

Substitutions: Not permitted.

Upward Coiling Service Doors

Wayne Dalton; Model 900 Rolling Service Door.

Slats:  Interlocking, roll-formed, metal slats.

- ~~~~~ MASTER NOTE ~~~~~~
Standard maximum width of 14 feet (4.27 m). For larger doors, contact manufacturer.
~~~ END OF MASTER NOTE ~~~~

Width:  << _______>>.

- ~~~~~ MASTER NOTE ~~~~~~
Standard maximum height of 14 feet (4.27 m). For larger doors, contact manufacturer.
~~~ END OF MASTER NOTE ~~~~

Height:  << _______>>.

Mounting:  << Surface-mounted on side indicated on drawings; or  Between jamb>>.

Opening Speed:  Door to operate at variable speed up to << 6 to 12 inches (152 to 305 mm)>> per second.

Closing Speed:  Door to operate at variable speed up to << 6 to 12 inches (152 to 305 mm)>> per second.

Operation Cycles:  Capable of operating for minimum << 20,000;  50,000;  100,000; or  200,000>> cycles. One operation cycle is complete when door is opened from closed position to fully open position and returned to closed position.

Available Warranty:

Door Only:  Two years.

Door and Operator Warranty:  Three years or 20,000 cycles, whichever comes first.

~~~~~ MASTER NOTE ~~~~~~
31 psf (1.5 kPa) wind load rating available only for 22-gauge steel doors up to 10 feet (3 m) in width, maximum. 20 psf (0.96 kPa) available for 22-gauge doors over 10 feet (3 m) wide.
24- and 26-gauge steel doors only available with 20 psf (0.96 kPa) wind load rating.
~~~ END OF MASTER NOTE ~~~~

Wind Load:  Design door assembly to withstand ultimate static pressure load of << 20 psf (0.96 kPa);  31 psf (1.48 kPa);  26 psf (1.25 kPa);  36 psf (1.72 kPa);  41 psf (1.96 kPa);  50 psf (2.39 kPa);  57 to 130 psf (2.73 to 6.22 kPa);  65 psf (3.11 kPa); or  68.9 psf (3.29 kPa)>>.

Curtain Material:  Galvanized steel. Staking lock system locks end of each slat from lateral movement.

~~~~~ MASTER NOTE ~~~~~~
Curved profile type C-187, 1.87-inch tall slat, for doors up to 15 feet 4 inches (4.67 m) wide, fabricated of: 1) 24 gauge galvanized steel.
2) 22 gauge galvanized steel.
3) 20 gauge galvanized steel.
4) 18 gauge galvanized steel.
5) 22 gauge stainless steel.
6) 20 gauge stainless steel.
7) 0.040 inch (1 mm) aluminum. Curved profile type C-275, 2.75-inch tall slat, for doors up to and between 15 feet 4 inches (4.67 m) and 18 feet 4 inches (5.59 m) wide, fabricated of: 1) 22 gauge galvanized steel.
2) 20 gauge galvanized steel.
3) 18 gauge galvanized steel.
4) 16 gauge galvanized steel.
5) 22 gauge stainless steel.
6) 20 gauge stainless steel.
7) 0.050 inch (1.29 mm) aluminum. Curved profile type C-275 for doors between 18 feet 4 inches (5.59 m) and 25 feet 4 inches (7.72 m) wide, fabricated of: 1) 20 gauge galvanized steel.
2) 18 gauge galvanized steel.
3) 16 gauge galvanized steel.
4) 20 gauge stainless steel.
5) 0.064 inch (1.63 mm) aluminum. Curved profile type C-275 for doors between 25 feet 4 inches (7.72 m) and 40 feet (12.19 m) wide, fabricated of: 1) 18 gauge galvanized steel.
2) 16 gauge galvanized steel.
3) 0.064 inch (1.63 mm) aluminum. Maximum width is 27 feet. Flat profile type F-265, 2.65-inch tall slat, for doors up to 18 feet 4 inches (5.59 m) wide, fabricated of: 1) 22 gauge galvanized steel.
2) 20 gauge galvanized steel.
3) 18 gauge galvanized steel.
4) 16 gauge galvanized steel.
5) 22 gauge stainless steel.
6) 20 gauge stainless steel.
7) 0.040 inch (1 mm) aluminum. Flat profile type F-265 for doors between 18 feet 4 inches (5.59 m) and 25 feet 4 inches (7.72 m) wide, fabricated of: 1) 20 gauge galvanized steel.
2) 18 gauge galvanized steel.
3) 16 gauge galvanized steel.
4) 20 gauge stainless steel.
5) 0.050 inch (1.29 mm) aluminum. Flat profile type F-265 for doors between 25 feet 4 inches (7.72 m) and 40 feet (12.19 m) wide, fabricated of: 1) 18 gauge galvanized steel.
2) 16 gauge galvanized steel.
3) 0.050 inch (1.29 mm) aluminum. Maximum width is 27 feet.
~~~ END OF MASTER NOTE ~~~~

Slat Profile:  << No.2, 2-inch (51 mm) curved profile;  No.17, 2-inch (51 mm) flat profile;  F-265; or  FE-265>>.

- ~~~~~ MASTER NOTE ~~~~~~
Size 1 by 10 inches (25 by 254 mm) on F-265 slat only.
~~~ END OF MASTER NOTE ~~~~

Fenestrated Slats:  << Not required;  Secur-Vent perforated slat;  5/8 by 3 inches (16 by 76 mm);  1 by 10 inches (25 by 254 mm);  5/8 by 3 inches (16 by 76 mm) with Plexiglass covers; or  1 by 10 inches (25 by 254 mm) with Plexiglass covers>>.

Finish:

Standard polyester base coat; << gray;  beige;  white; or  brown>> color.

G-90 (Z275) galvanized<< ; primed gray; or  None - N/A>>.

Bottom Bar:  Steel.

- ~~~~~ MASTER NOTE ~~~~~~
Galvanized Steel: Double angle, single angle.
Stainless Steel: Double angle.
Aluminum: Double angle, extruded T, extruded tube.
~~~ END OF MASTER NOTE ~~~~

Profile:  Double angle.

Finish:  << Galvanized, primed black;  Black anodized;  Bronze anodized;  Hot-dip galvanized;  PowderGuard Premium powder coat;  PowderGuard Textured powder coat;  PowderGuard Zinc powder coat;  Stainless No.4 satin; or  Stainless No.2B mill>>.

Locking Options to Include:  << None;  Slide lock;  Cylinder; or  Best cylinder>>.

Lock Locations:  << Both jambs;  Left only; or  Right only>>.

Lock Access:  << Coil side; or  Opposite coil side>>.

Weatherstripping and Seals:

- ~~~~~ MASTER NOTE ~~~~~~
Bottom seal astragal comes standard.
~~~ END OF MASTER NOTE ~~~~

Bottom Seal Astragal:  << Required; or  Not required>>.

Guide Surface Weatherstrip:  << Angled brush seal;  Vinyl seal; or  Not required>>.

Lintel Brush Seal:  << Interior;  Exterior;  Interior and exterior; or  Not required>>.

Interior Hood Baffle:  << Required; or  Not required>>.

Side Guides, Channels:  Constructed of << steel;  304 stainless steel; or  aluminum>> with members fully bolted together.

Finish:  << Mill finish;  Clear anodized;  Bronze anodized;  Black anodized;  Powder coat;  Stainless No.4 satin;  Hot-dip galvanized;  Galvanized, primed black;  PowderGuard Textured powder coat;  PowderGuard Zinc powder coat; or  Stainless No.2B mill>>.

Color:  << Match curtain;  Black; or  _____>>.

Brackets:  << Steel; or  304 stainless steel>> to support counterbalance and curtain.

Finish:  << Hot-dip galvanized;  Galvanized, primed black;  Stainless No.4 satin;  Powder coat;  PowderGuard Premium powder coat; _____ color;  PowderGuard Textured powder coat; _____ color; or  PowderGuard Zinc powder coat; _____ color>>.

Color:  << Match curtain; or  _____>>.

Counterbalance:  Helical torsion spring type, housed in steel tube or pipe barrel and supporting curtain with deflection limited to << 0.03 inch per foot (1:400 mm/sec)>> of span. Adjustable spring tension required.

Hood:  << Not required;  24 gauge, 0.028 inch stainless steel (0.63 mm stainless steel);  24 gauge, 0.028 inch galvanized steel (0.63 mm galvanized steel);  22 gauge, 0.025 inch B&S aluminum (0.64 mm B&S aluminum); or  _____ gauge, _____ inch (_____ mm)>>.

Finish:  << Galvanized, primed to match curtain;  Hot-dip galvanized;  Clear anodized;  Standard polyester base coat; gray color;  Bronze anodized;  Standard polyester base coat; tan color;  Mill finish;  Standard polyester base coat; white color;  Powder coat;  _____   color;  Standard polyester base coat; brown color;  Stainless No. 4 satin;  Gray-primed galvanized G90 (Z275);  Black anodized; or  PowderGuard Premium powder coat; _____ color>>.

- ~~~~~ MASTER NOTE ~~~~~~
Manual push-up available up to 8 by 8 feet (2438 by 2438 mm). Chain hoist over 8 by 8 feet (2438 by 2438 mm).
Bracket-mounted crank available up to 12 feet 4 inches (3759 mm) in height or 10 feet 4 inches (3149 mm) in width.
Wall crank not available if between-jamb mounted; available up to 16 feet 4 inches (4978 mm) in width or 14 feet 4 inches (4369 mm) in height.
~~~ END OF MASTER NOTE ~~~~

Manual Operation:  << Push-up;  Chain hoist;  Bracket-mounted crank; or  Wall-mounted crank>>.

Motor Operation:  << Not required; or  Provide UL-listed electric operator; size as recommended by manufacturer to move door in either direction at minimum 8 inches (203 mm), maximum 1 foot (305 mm) per second>>.

Manual Override:  << Hoist;  Hoist and jackshaft release; or  Jackshaft release>>.

Timer to Close:  << Not required; or  Automatic closing controlled by adjustable hold-open time delay>>.

Operation Supply Voltage:  << 115/208/230V 1-phase 60Hz;  208/230/460V 3 phase 60Hz;  575V 3-phase 60Hz;  220V 1-phase 50Hz;  220V 3-phase 50Hz; or  400V 3-phase 50Hz>>.

Signaling Device:  << Horn and strobe combination; or  Traffic warning light>>.

Actuation Device:  Provide << push button;  key switch;  pull cord;  loop detector;  motion detector;  treadle switch; and  radio control>>.

Motor Mounting:  << Wall-mounted; or  Front of hood>>, << right-hand side; or  left-hand side>>.

Motor Enclosure:  << Not required;  NEMA 4-12 watertight and oiltight;  NEMA 4X corrosion-resistant;  Totally enclosed, fan-cooled motor; or  Totally enclosed, non-ventilated>>.

Obstruction Safety Detection:  Constant contact button only.

Obstruction Safety Detection:

Primary, Monitored:

Photo Eyes:  << Reflective photo-eyes;  Thru-beam photo-eyes; or  NEMA 4X photo-eyes>>.

Light Curtain:  << 3 feet (0.91 m);  6 feet (1.83 m); or  _____ feet (_____ m)>>.

Safety Edge:  << 2-wire reversing safety edge;  Wireless reversing safety edge; or  ______>>.

Secondary, Non-Monitored:

Photo Eyes:  << Reflective photo-eyes;  Thru-beam photo-eyes; or  _____>>.

Light Curtain:  << 3 feet (0.9 m);  6 feet (1.8 m); or  _____ feet (_____ m)>>.

Safety Edge:  << 2-wire reversing safety edge; or  ______>>.

PART 3 EXECUTION

Examination

Verify << existing conditions; and  _______>> meet manufacturer's requirements before starting work.

Verify opening sizes, tolerances, and conditions are acceptable.

Installation

Install in accordance with manufacturer's written instructions.

Use anchorage devices to securely fasten assembly to wall construction and building structure without distortion or stress.

Securely and rigidly brace components suspended from structure.<<  Secure guides to structural members only.;    _____ .; or  None - N/A>>

Fit and align assembly, including hardware. Level and plumb to provide smooth operation.

Coordinate installation of electrical service; see Section << 260583>>.

Install enclosure and perimeter trim.

Tolerances

Maintain dimensional tolerances and alignment with adjacent work.

Maximum Variation from Plumb:  << 1/16 inch (1.6 mm); or  ___ inch (___ mm)>>.

Maximum Variation from Level:  << 1/16 inch (1.6 mm); or  ___ inch (___ mm)>>.

Longitudinal or Diagonal Warp:  Plus or minus << 1/8 inch per 10 feet (3.2 mm per 3 m); or  ___ inch per 10 feet (___ mm per 3 m)>> straight edge.

Adjusting

Adjust operating assemblies for smooth and noiseless operation.

Cleaning

See Section << 017000 - Execution and Closeout Requirements>> for additional requirements.

Clean installed components.

Remove labels and visible markings.

Protection

Protect finishes until completion of project.

Touch up damaged finishes after Date of Substantial Completion.

- END OF SECTION